## InfraPower R784
OID | Name | Access Type | Description
.1.3.6.1.4.1.34550.20 | InfraPower | N/A | N/A
.1.3.6.1.4.1.34550.20.1 | ipDongle | N/A | N/A
.1.3.6.1.4.1.34550.20.1.1 | ipDongleAdmin | N/A | N/A
.1.3.6.1.4.1.34550.20.1.1.1.0 | ipdongleModel | Read Only | InfraPower
.1.3.6.1.4.1.34550.20.1.1.5.0 | ipdongleName | Read / Write | The name of the IP Dongle Length : 4 to 16 char. Valid characters are( 0 ~ 9 ) , ( a ~ z ) , ( A ~ Z ) , ( _ ) , ( - ) and ( . )
.1.3.6.1.4.1.34550.20.1.1.6.0 | ipdongleLocation | Read / Write | The Location of the IP Dongle Length : 4 to 16 char. Valid characters are( 0 ~ 9 ) , ( a ~ z ) , ( A ~ Z ) , ( _ ) , ( - ) and ( . )
.1.3.6.1.4.1.34550.20.1.1.8.0 | ipdongleMacAddress | Read Only | The MAC address of the IP Dongle
.1.3.6.1.4.1.34550.20.1.1.9.0 | ipdongleIpAddressIpv4 | Read Only | The IPv4 address of the IP Dongle
.1.3.6.1.4.1.34550.20.1.1.10.0 | ipdongleSubnetIpv4 | Read Only | The IPv4 subnet of the IP Dongle
.1.3.6.1.4.1.34550.20.1.1.11.0 | ipdongleGatewayIpv4 | Read Only | The IPv4 gateway of the IP Dongle
.1.3.6.1.4.1.34550.20.2 | pduGroup | N/A | N/A
.1.3.6.1.4.1.34550.20.2.1 | pduAdmin | N/A | N/A
.1.3.6.1.4.1.34550.20.2.1.1 | pduTable | N/A | Table of PDU
.1.3.6.1.4.1.34550.20.2.1.1.1 | pduEntry | N/A | Table Entries of PDU
.1.3.6.1.4.1.34550.20.2.1.1.1.1.[1..32] | pduIndex | Read Only | PDU level in the Group , Single Feed PDU : Level : 1 to 16 .1.3.6.1.4.1.34550.20.2.1.1.1.1.1 = PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.1.16 = PDU level 16 Dual Feed PDU : Level : 1 to 32 .1.3.6.1.4.1.34550.20.2.1.1.1.1.1 = Feed 1 of PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.1.17 = Feed 2 of PDU level 1
.1.3.6.1.4.1.34550.20.2.1.1.1.2.[1..32] | pduModel | Read Only | PDU model No. , Single Feed PDU : Level : 1 to 16 .1.3.6.1.4.1.34550.20.2.1.1.1.2.1 = PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.2.16 = PDU level 16 Dual Feed PDU : Level : 1 to 32 .1.3.6.1.4.1.34550.20.2.1.1.1.2.1 = Feed 1 of PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.2.17 = Feed 2 of PDU level 1 ( Feed 1 and Feed 2 of Dual Feed PDU will show the same PDU model )
.1.3.6.1.4.1.34550.20.2.1.1.1.3.[1..32] | pduID | Read Only | PDU unique identifier , Single Feed PDU : Level : 1 to 16 .1.3.6.1.4.1.34550.20.2.1.1.1.3.1 = PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.3.16 = PDU level 16 Dual Feed PDU : Level : 1 to 32 .1.3.6.1.4.1.34550.20.2.1.1.1.3.1 = Feed 1 of PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.3.17 = Feed 2 of PDU level 1
.1.3.6.1.4.1.34550.20.2.1.1.1.4.[1..32] | pduSerialNo | Read Only | PDU Serial no. ( This OID is NOT applicable to PDU with 1.8" color LCD & the value of the OID returned will be BLANK ), Single Feed PDU : Level : 1 to 16 .1.3.6.1.4.1.34550.20.2.1.1.1.4.1 = PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.4.16 = PDU level 16 Dual Feed PDU : Level : 1 to 32 .1.3.6.1.4.1.34550.20.2.1.1.1.4.1 = Feed 1 of PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.4.17 = Feed 2 of PDU level 1
.1.3.6.1.4.1.34550.20.2.1.1.1.6.[1..32] | pduName | Read / Write | The name of PDU , Level : 1 to 16 Length : 1 to 16 char. Valid characters are( 0 ~ 9 ) , ( a ~ z ) , ( A ~ Z ) , ( _ ) , ( - ) , ( . ) and ( space ) Single Feed PDU : Level : 1 to 16 .1.3.6.1.4.1.34550.20.2.1.1.1.6.1 = PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.6.16 = PDU level 16 Dual Feed PDU : Level : 1 to 32 .1.3.6.1.4.1.34550.20.2.1.1.1.6.1 = Feed 1 of PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.6.17 = Feed 2 of PDU level 1 ( Feed 1 and Feed 2 of Dual Feed PDU will show the same PDU name )
.1.3.6.1.4.1.34550.20.2.1.1.1.7.[1..32] | pduLocation | Read / Write | The Location of PDU , Level : 1 to 16 Length : 1 to 16 char. Valid characters are( 0 ~ 9 ) , ( a ~ z ) , ( A ~ Z ) , ( _ ) , ( - ) , ( . ) and ( space ) Single Feed PDU : Level : 1 to 16 .1.3.6.1.4.1.34550.20.2.1.1.1.7.1 = PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.7.16 = PDU level 16 Dual Feed PDU : Level : 1 to 32 .1.3.6.1.4.1.34550.20.2.1.1.1.7.1 = Feed 1 of PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.7.17 = Feed 2 of PDU level 1 ( Feed 1 and Feed 2 of Dual Feed PDU will show the same PDU Location )
.1.3.6.1.4.1.34550.20.2.1.1.1.8.[1..32] | pduGroupNumber | Read / Write | The number indicates the IP dongle group the PDU belongs to when using InfraPower Management Software. Group number : from 000 to 240
.1.3.6.1.4.1.34550.20.2.1.1.1.13.[1..32] | pduMainLoadVoltage | Read Only | The voltage measured of the PDU in tenth of Volts , Single Feed PDU : Level : 1 to 16 .1.3.6.1.4.1.34550.20.2.1.1.1.13.1 = PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.13.16 = PDU level 16 Single Phase PDU : 2215 = 221.5 VAC 3 Phase PDU : 2204 ( 2201 , 2205 , 2206 ) = 1st 4 digit is the average voltage of all the phase. The figure in the bracket is the voltage of phase 1 , phase 2 & phase 3 respectively Dual Feed PDU : Level : 1 to 32 .1.3.6.1.4.1.34550.20.2.1.1.1.1.1 = Feed 1 of PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.1.17 = Feed 2 of PDU level 17 Single Phase PDU : 2215 = 221.5 VAC
.1.3.6.1.4.1.34550.20.2.1.1.1.14.[1..32] | pduMainLoadAmp | Read Only | The current load ampere of the PDU measured in tenth of amp. 0 = 0.0A , 1 = 0.1A , 135 = 13.5A Single Feed PDU : Level : 1 to 16 .1.3.6.1.4.1.34550.20.2.1.1.1.14.1 = PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.14.16 = PDU level 16 Dual Feed PDU : Level : 1 to 32 .1.3.6.1.4.1.34550.20.2.1.1.1.14.1 = Feed 1 of PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.14.17 = Feed 2 of PDU level 1
.1.3.6.1.4.1.34550.20.2.1.1.1.16.[1..32] | pduMainPowerFactor | Read Only | The power factor of the PDU measured in hundredth 000 = 0 , 001 = 0.01 , 055 = 0.55 , 100 = 1.0 Single Feed PDU : Level : 1 to 16 .1.3.6.1.4.1.34550.20.2.1.1.1.16.1 = PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.16.16 = PDU level 16 Dual Feed PDU : Level : 1 to 32 .1.3.6.1.4.1.34550.20.2.1.1.1.16.1 = Feed 1 of PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.16.17 = Feed 2 of PDU level 1
.1.3.6.1.4.1.34550.20.2.1.1.1.17.[1..32] | pduMainActivePower | Read Only | The power consumption of the PDU measured in hundred-thousandth of kW Range : 0000000 to 9999999 0 = 0kW , 25 = 0.00025kW , 123 = 0.00123kW , 1234567 = 12.34567kW Single Feed PDU : Level : 1 to 16 .1.3.6.1.4.1.34550.20.2.1.1.1.17.1 = PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.17.16 = PDU level 16 Dual Feed PDU : Level : 1 to 32 .1.3.6.1.4.1.34550.20.2.1.1.1.17.1 = Feed 1 of PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.17.17 = Feed 2 of PDU level 1
.1.3.6.1.4.1.34550.20.2.1.1.1.18.[1..32] | pduMainApparentPower | Read Only | The power consumption of the PDU measured in hundred-thousandth of kVA Range : 0000000 to 9999999 0 = 0VA , 25 = 0.25VA, 123 = 1.23VA , 1234567 = 12345.67VA Single Feed PDU : Level : 1 to 16 .1.3.6.1.4.1.34550.20.2.1.1.1.18.1 = PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.18.16 = PDU level 16 Dual Feed PDU : Level : 1 to 32 .1.3.6.1.4.1.34550.20.2.1.1.1.18.1 = Feed 1 of PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.18.17 = Feed 2 of PDU level 1
.1.3.6.1.4.1.34550.20.2.1.1.1.19.[1..32] | pduMainCumulativeEnergy | Read Only | The accumulated energy consumption of the PDU in hundredth of kWh Range : 00000000 to 99999999 0 = 0.00kWh , 123 = 1.23kWh , 12345 = 123.45kWh , 12345678 = 123456.78kWh Single Feed PDU : Level : 1 to 16 .1.3.6.1.4.1.34550.20.2.1.1.1.19.1 = PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.19.16 = PDU level 16 Dual Feed PDU : Level : 1 to 32 .1.3.6.1.4.1.34550.20.2.1.1.1.19.1 = Feed 1 of PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.19.17 = Feed 2 of PDU level 1
.1.3.6.1.4.1.34550.20.2.1.1.1.20.[1..32] | pduRealClock | Read Only | The real time of the PDU. Format : YYMMDDHHNNSSW 1503281759596 = 2015-Mar-28 17:59:59 Saturaday
.1.3.6.1.4.1.34550.20.2.1.1.1.24 | circuits | N/A
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1 | circuitTable | N/A | Table of circuits / banks
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1 | circuitTablEntry | N/A | Table entries of circuit / bank
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.1.[1..32].[1..6] | circuitIndex | Read Only | The ID of the PDU's circuit / bank Single Feed PDU : Single Phase : 1 = Circuit A , 2= Circuit B 63A Single Phase : 1 = bank 1 , 2 = bank 2 , 3 = bank 3 , 4 = bank 4 3 Phase : 1 = bank 1 , 2 = bank 2 , 3 = bank 3 , 4 = bank 4, 5 = bank 5 , 6 = bank 6 Dual Feed PDU : Single Phase : .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.1.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.1.32.1 = circuit A of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.2.[1..32].[1..6] | circuitRatedAmp | Read Only | The input current rating of the PDU's circuit / bank in tenth of amp. Single Feed PDU : 100 = 10.0A , 160 = 16.0A , 200 = 20.0A Dual Feed PDU : .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.2.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.2.32.1 = circuit A of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.4.[1..32].[1..6] | circuitName | Read Only | The name of the circuit Single Feed PDU : Single Phase : Circuit A , Circuit B 63A Single Phase : Circuit B1 , Circuit B2 , Circuit B3 , Circuit B4 3 Phase ( 400V ) : L1-B1, L1-B2 , L2-B3, L2-B4, L3-B5, L3-B6 3 Phase ( 208V ) : B1 , B2 , B3 , B4 , B5 , B6 Dual Feed PDU : Single Phase : PDU I - A , PDU I - B , PDU II - A , PDU II - B
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.5.[1..32].[1..6] | circuitState | Read Only | The status of the PDU's circuit / bank. Single Feed PDU : 0 = Normal, 1 = Alarm , 2 = Rising alert , 3 = Low alert , 4 = circuit not exist Dual Feed PDU : .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.5.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.5.32.1 = circuit A of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.6.[1..32].[1..6] | circuitLoadVoltage | Read Only | The voltage of the PDU's circuit / bank measured in tenth of volt. 0000 = 0.0VAC , 1100 = 110.0VAC , 2225 = 222.5VAC Dual Feed PDU : .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.6.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.6.32.1 = circuit A of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.7.[1..32].[1..6] | circuitLoadAmp | Read Only | The current load ampere of the PDU's circuit / bank measured in tenth of amp. 000 = 0.0A , 001 = 0.01A , 105 = 10.5A Dual Feed PDU : .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.7.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.7.32.1 = circuit A of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.9.[1..32].[1..6] | circuitPowerFactor | Read Only | The power factor of the PDU's circuit measured in hundredth 000 = 0 , 001 = 0.01 , 055 = 0.55 , 100 = 1.0 Single Feed PDU : Level : 1 to 16 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.9.1.1 = circuit A of PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.9.16.2 = circuit B of PDU level 16 Dual Feed PDU : Level : 1 to 32 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.9.1.1 = circuit A of Feed 1 of PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.9.17.2 = circuit B of Feed 2 of PDU level 1
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.10.[1..32].[1..6] | circuitActivePower | Read Only | The power consumption of the PDU's circuit measured in hundred-thousandth of kW Range : 0000000 to 9999999 0 = 0kW , 25 = 0.00025kW , 123 = 0.00123kW , 1234567 = 12.34567kW Single Feed PDU : Level : 1 to 16 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.10.1.1 = circuit A of PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.10.16.2 = circuit B of PDU level 16 Dual Feed PDU : Level : 1 to 32 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.10.1.1 = circuit A of Feed 1 of PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.10.17.2 = circuit B of Feed 2 of PDU level 1
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.11.[1..32].[1..6] | circuitApparentPower | Read Only | The power consumption of the PDU's circuit measured in hundred-thousandth of kVA Range : 0000000 to 9999999 0 = 0VA , 25 = 0.25VA, 123 = 1.23VA , 1234567 = 12345.67VA Single Feed PDU : Level : 1 to 16 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.11.1.1 = circuit A of PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.11.16.2 = circuit B of PDU level 16 Dual Feed PDU : Level : 1 to 32 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.11.1.1 = circuit A of Feed 1 of PDU level 1 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.11.17.2 = circuit B of Feed 2 of PDU level 1
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.12.[1..32].[1..6] | circuitLoadPeakAmp | Read Only | The peak load ampere of the PDU's circuit / bank recorded in tenth of amp with timestamp. 150330105959@081 = 2015-Mar-30 10:59:59 , 8.1A Dual Feed PDU : .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.12.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.12.32.1 = circuit A of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.13.[1..32].[1..6] | circuitCumulativeEnergy | Read Only | The accumulated energy consumption of the PDU's circuit / bank in hundredth of kWh with timestamp Range : 00000000 to 99999999 150330105959@09999999 = 2015-Mar-30 10:59:59 , 99999.99kWh Dual Feed PDU : .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.13.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.13.32.1 = circuit A of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.14.[1..32].[1..6] | circuitLoadPeakAmpReset | Read / Write | To reset the PDU's circuit / bank peak amp to zero with timestamp updated. Set : 1 = confirm to reset Dual Feed PDU : .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.14.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.14.32.1 = circuit A of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.15.[1..32].[1..6] | circuitBreakerStateCopy | Read Only | The circuit breaker state of the PDU. 0 = normal , 1 = tripped Dual Feed PDU : .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.15.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.15.32.1 = circuit A of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.16.[1..32].[1..6] | circuitLoadAmpAlarmThresh | Read / Write | To set the current load ampere alarm threshold of the PDU's circuit / bank in tenth of amp. 000 = disable , 001 = 0.1A , 050 = 5.0A , 130 = 13.0A Dual Feed PDU : .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.16.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.16.32.1 = circuit A of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.17.[1..32].[1..6] | circuitLoadAmpRisingAlertThresh | Read / Write | To set the current load ampere rising alert threshold of the PDU's circuit / bank in tenth of amp. 000 = disable , 001 = 0.1A , 050 = 5.0A , 130 = 13.0A Dual Feed PDU : .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.17.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.17.32.1 = circuit A of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.18.[1..32].[1..6] | circuitLoadAmpLowAlertThresh | Read / Write | To set the current load ampere low alert threshold of the PDU's circuit / bank in tenth of amp. 000 = disable , 001 = 0.1A , 050 = 5.0A , 130 = 13.0A Dual Feed PDU : .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.18.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.18.32.1 = circuit A of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.19.[1..32].[1..6] | circuitCumulativeEnergyReset | Read / Write | To reset the PDU's circuit / bank cumulative energy to zero with timestamp updated. Set : 1 = confirm to reset Dual Feed PDU : .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.19.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.19.32.1 = circuit A of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.25 | circuitBreakers | N/A
.1.3.6.1.4.1.34550.20.2.1.1.1.25.1 | circuitBreakerTable | N/A | Table of circuit breaker
.1.3.6.1.4.1.34550.20.2.1.1.1.25.1.1 | circuitBreakerTableEntry | N/A | Table entries of circuit breaker
.1.3.6.1.4.1.34550.20.2.1.1.1.25.1.1.1.[1..32].[1..6] | circuitBreakerIndex | Read Only | The ID of the PDU's circuit breaker. Single Phase : 1 = circuit A's circuit breaker, 2 = circuit B's circuit breaker 63A Single Phase : 1 = bank 1's circuit breaker , 2 = bank 2's circuit breaker , 3 = bank 3's circuit breaker , 4 = bank 4's circuit breaker 3 Phase : 1 = bank 1's circuit breaker , 2 = bank 2's circuit breaker , 3 = bank 3's circuit breaker , 4 = bank 4's circuit breaker , 5 = bank 5's circuit breaker , 6 = bank 6's circuit breaker Dual Feed PDU : .1.3.6.1.4.1.34550.20.2.1.1.1.25.1.1.1.16.1 = circuit A's circuit breaker of Feed 1 of PDU level 16 .1.3.6.1.4.1.34550.20.2.1.1.1.25.1.1.1.32.1 = circuit A's circuit breaker of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.25.1.1.2.[1..32].[1..6] | circuitBreakerRatedAmp | Read Only | The current rating of the PDU's circuit breaker in tenth of amp. 100 = 10.0A , 160 = 16.0A , 200 = 20.0A Dual Feed PDU : .1.3.6.1.4.1.34550.20.2.1.1.1.25.1.1.2.16.1 = circuit A of Feed 1 of PDU level 16 .1.3.6.1.4.1.34550.20.2.1.1.1.25.1.1.2.32.1 = circuit A of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.25.1.1.4.[1..32].[1..6] | circuitBreakerState | Read Only | The circuit breaker state of the PDU. 0 = normal , 1 = tripped Dual Feed PDU : .1.3.6.1.4.1.34550.20.2.1.1.1.25.1.1.4.16.1 = circuit A's circuit breaker of Feed 1 of PDU level 16 .1.3.6.1.4.1.34550.20.2.1.1.1.25.1.1.4.32.1 = circuit A's circuit breaker of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.26 | outlets | N/A
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1 | stdOutletTable | N/A | Table of non - C19 outlet
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1 | stdOutletTableEntry | N/A | Table entries of non - C19 outlet
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.1.[1..32].[1..72] | stdOutletIndex | Read Only | The ID of the PDU's non - C19 outlet. Range : 1 to 72. 1 = outlet 01, 72 = outlet 72
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.2.[1..32].[1..72] | stdOutletCircuit | Read Only | The circuit of the outlet belongs to - Single phase : 1 = circuit A , 2 = circuit B 63A single phase : 1 = bank 1 , 2 = bank 2 , 3 = bank , 4 = bank 4 3 Phase : 1 = bank 1 , 2 = bank 2 , 3 = bank , 4 = bank 4 , 5 = bank 5 , 6 = bank 6 Dual Feed PDU : .1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.2.16.1 = outlet 1 of Feed 1 of PDU level 16 .1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.2.32.16 = outlet 16 ofFeed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.3.[1..32].[1..72] | stdOutletType | Read Only | The type of non - C19 outlet. 1 = IEC C13 , 3 = BS1363 , 4 = NEMA 5-204 , 5 = Schuko , 6 = AS 31125 , 7 = French , 8 = 60309-16A , 9 =60309-32A
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.4.[1..32].[1..72] | stdOutletName | Read / Write | The name of the outlet. Range : 4 to 16 char. Valid characters are( 0 ~ 9 ) , ( a ~ z ) , ( A ~ Z ) , ( _ ) , ( - ) , ( . ) and ( space )
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.7.[1..32].[1..72] | stdOutletPowerStatus | Read / Write | The power state of the outlet. 0 = OFF , 1 = ON Set : 0 = switch off , 1 = switch on
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.8.[1..32].[1..72] | stdOutletAlarmState | Read Only | The alarm state of the outlet. 0 = Normal, 1 = Alarm , 2 = Rising alert , 3 = Low alert
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.9.[1..32].[1..72] | stdOutletLoadAmp | Read Only | The current load ampere of the outlet measured in tenth of amp. 000 = 0.0A , 001 = 0.01A , 105 = 10.5A , " --- " = immeasurable
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.10.[1..32].[1..72] | stdOutletEnergy | Read Only | The power consumption of the OUTLET measured in hundred-thousandth of kW. Range : 0000000 to 9999999 0 = 0kW , 25 = 0.00025kW , 123 = 0.00123kW , 1234567 = 12.34567kW
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.11.[1..32].[1..72] | stdOutletPeakAmp | Read Only | The peak load ampere of the outlet recorded in tenth of amp with timestamp. 150330105959@031 = 2015-Mar-30 10:59:59 , 3.1A
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.12.[1..32].[1..72] | stdOutletCumulativeEnergy | Read Only | The accumulated energy consumption of the outlet in hundredth of kWh with timestamp Range : 00000000 to 99999999 150330105959@09999999 = 2015-Mar-30 10:59:59 , 99999.99kWh
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.13.[1..32].[1..72] | stdOutletLoadAmpAlarmThresh | Read / Write | To set the current load ampere alarm threshold of the outlet in tenth of amp. 000 = disable , 001 = 0.1A , 050 = 5.0A , 130 = 13.0A
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.14.[1..32].[1..72] | stdOutletLoadAmpRisingAlertThresh | Read / Write | To set the current load ampere rising alert threshold of the outlet in tenth of amp. 000 = disable , 001 = 0.1A , 050 = 5.0A , 130 = 13.0A
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.15.[1..32].[1..72] | stdOutletLoadAmpLowAlertThresh | Read / Write | To set the current load ampere low alert threshold of the outlet in tenth of amp. 000 = disable , 001 = 0.1A , 050 = 5.0A , 130 = 13.0A
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.16.[1..32].[1..72] | stdOutletPeakAmpReset | Read / Write | To reset the outlet peak amp reacord to zero with timestamp updated. Set : 1 = confirm to reset
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.17.[1..32].[1..72] | stdOutletCumulativeEnergyReset | Read / Write | To reset the outlet accumulated energy consumpiton record to zero with timestamp updated. Set : 1 = confirm to reset
.1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.18.[1..32].[1..72] | stdOutletPowerUpSequenceDelay | Read / Write | To set the sequential power up interval between outlet in second. Range : 1 to 10 sec. Set : 0 = 1 sec , 5 = 6 sec , 9 = 10 sec
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2 | c19OutletTable | N/A | Table of C19 outlet
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1 | c19OutletTableEntry | N/A | Table entries of C19 outlet
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.1.[1..32].[1..72] | c19OutletIndex | Read Only | The ID of the PDU's C19 outlet. Range : 1 to 72. 1 = outlet C01, 72 = outlet C72
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.2.[1..32.[1..72] | c19OutletCircuit | Read Only | The circuit of the outlet belongs to - Single phase : 1 = circuit A , 2 = circuit B 63A single phase : 1 = bank 1 , 2 = bank 2 , 3 = bank , 4 = bank 4 3 Phase : 1 = bank 1 , 2 = bank 2 , 3 = bank , 4 = bank 4 , 5 = bank 5 , 6 = bank 6 Dual Feed PDU : .1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.2.16.1 = outlet C1 of Feed 1 of PDU level 16 .1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.2.32.16 = outlet C16 of Feed 2 of PDU level 16
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.3.[1..32].[1..72] | c19OutletType | Read Only | The type of C19 outlet. 2 = IEC C19
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.4.[1..32].[1..72] | c19OutletName | Read / Write | The name of the outlet. Range 4 to 16 char. Valid characters are( 0 ~ 9 ) , ( a ~ z ) , ( A ~ Z ) , ( _ ) , ( - ) , ( . ) and ( space )
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.7.[1..32].[1..72] | c19OutletPowerStatus | Read / Write | The power state of the outlet. 0 = OFF , 1 = ON Set : 0 = switch off , 1 = switch on
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.8.[1..32].[1..72] | c19OutletAlarmState | Read Only | The alarm state of the outlet. 0 = Normal, 1 = Alarm , 2 = Rising alert , 3 = Low alert
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.9.[1..32].[1..72] | c19OutletLoadAmp | Read Only | The current load ampere of the outlet measured in tenth of amp. 000 = 0.0A , 001 = 0.01A , 105 = 10.5A , " --- " = immeasurable
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.10.[1..32].[1..72] | c19OutletEnergy | Read Only | The power consumption of the OUTLET measured in hundred-thousandth of kW. Range : 0000000 to 9999999 0 = 0kW , 25 = 0.00025kW , 123 = 0.00123kW , 1234567 = 12.34567kW
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.11.[1..32].[1..72] | c19OutletPeakAmp | Read Only | The peak load ampere of the outlet recorded in tenth of amp with timestamp. 150330105959@031 = 2015-Mar-30 10:59:59 , 3.1A
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.12.[1..32].[1..72] | c19OutletCumulativeEnergy | Read Only | The accumulated energy consumption of the outlet in hundredth of kWh with timestamp Range : 00000000 to 99999999 150330105959@09999999 = 2015-Mar-30 10:59:59 , 99999.99kWh
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.13.[1..32].[1..72] | c19OutletLoadAmpAlarmThresh | Read / Write | To set the current load ampere alarm threshold of the outlet in tenth of amp. 000 = disable , 001 = 0.1A , 050 = 5.0A , 130 = 13.0A
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.14.[1..32].[1..72] | c19OutletLoadAmpRisingAlertThresh | Read / Write | To set the current load ampere rising alert threshold of the outlet in tenth of amp. 000 = disable , 001 = 0.1A , 050 = 5.0A , 130 = 13.0A
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.15.[1..32].[1..72] | c19OutletLoadAmpLowAlertThresh | Read / Write | To set the current load ampere low alert threshold of the outlet in tenth of amp. 000 = disable , 001 = 0.1A , 050 = 5.0A , 130 = 13.0A
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.16.[1..32].[1..72] | c19OutletPeakAmpReset | Read / Write | To reset the outlet peak amp reacord to zero with timestamp updated. Set : 1 = confirm to reset
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.17.[1..32].[1..72] | c19OutletCumulativeEnergyReset | Read / Write | To reset the outlet accumulated energy consumpiton record to zero with timestamp updated. Set : 1 = confirm to reset
.1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.18.[1..32].[1..72] | c19OutletPowerUpSequenceDelay | Read / Write | To set the sequential power up interval between outlet in second. Range : 1 to 10 sec. Set : 0 = 1 sec , 5 = 6 sec , 9 = 10 sec
.1.3.6.1.4.1.34550.20.2.1.1.1.27 | THSensors | N/A
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1 | THSensorsTable | N/A | Table of TH sensors
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1 | THSensorsTableEntry | N/A | Table entries of TH sensors
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.1.[1..16].[1..2] | THSensorIndex | Read Only | The ID of TH sensors. 1 = TH 1 , 2 = TH 2
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.3.[1..16].[1..2] | THSensorLocation | Read / Write | The location of TH sensor. Range : 4 to 16 char. Valid characters are( 0 ~ 9 ) , ( a ~ z ) , ( A ~ Z ) , ( _ ) , ( - ) and ( . )
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.4.[1..16].[1..2] | THSensorType | Read Only | The type of the sensor. 1 = Temp. sensor , 2 = Temp + Humid sensor
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.5.[1..16].[1..2] | THSensorConnState | Read Only | The connection status of the sensor. 0 = disconnected , 1 = connected
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.6.[1..16].[1..2] | THSensorAlarmState | Read Only | The alarm state of the sensor. 0 = normal , 1 = humid sensor alarm only , 10 = temp. sensor alarm only , 11 = temp + humid sensor alarm
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.7.[1..16].[1..2] | tempSensorValue | Read Only | The temp. measured in tenth of Degree Celsius 0 = 0C , 10 = 1C , 123 = 12.3C , 999 = 99.9C
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.8.[1..16].[1..2] | tempSensorValueStr | Read Only | The temp. measured in tenth of Degree Celsius ---- = disconnected , 0000 = 0C , 0010 = 1C , 0123 = 12.3C , 0999 = 99.9C
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.9.[1..16].[1..2] | tempSensorUpperAlarmThresh | Read / Write | The temp. alarm threshold in tenth of Degree Celsius Set : 0000 = 0C , 0010 = 1C , 0123 = 12.3C , 0999 =99.9C
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.10.[1..16].[1..2] | tempSensorLowerAlarmThresh | Read Only | The temp. alarm threshold in tenth of Degree Celsius 0000 = 0C , 0010 = 1C , 0123 = 12.3C , 0999 =99.9C
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.11.[1..16].[1..2] | humiSensorValue | Read Only | The relative humidity measured in tenth of percentage. 0 = 0% , 1 = 0.1% , 255 = 25.5% , 999 = 99.9%
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.12.[1..16].[1..2] | humiSensorValueStr | Read Only | The relative humidity measured in tenth of percentage. ---- = disconnected , 000 = 0% , 001 = 0.1% , 025 = 2.5% , 999 = 99.9%
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.13.[1..16].[1..2] | humiSensorUpperAlarmThresh | Read / Write | The relative humidity alarm threshold in tenth of percentage Set : 000 = 0% , 001 = 0.1% , 025 = 2.5% , 999 = 99.9%
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.14.[1..16].[1..2] | humiSensorLowerAlarmThresh | Read Only | The relative humidity alarm threshold in tenth of percentage 000 = 0% , 001 = 0.1% , 025 = 2.5% , 999 = 99.9%
.1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.15.[1..16].[1..2] | THSensorActivation | Read / Write | The activation state of the Temp. or Temp. & humid. Sensor. Set : 0 = deactivated , 1 = activated
.1.3.6.1.4.1.34550.20.2.1.1.1.28 | rCMSensors | N/A
.1.3.6.1.4.1.34550.20.2.1.1.1.28.1 | rCMSensorTable | N/A | Table of RCM Sensor
.1.3.6.1.4.1.34550.20.2.1.1.1.28.1.1 | rCMSensorTableEntry | N/A | Table entries of RCM Sensor
.1.3.6.1.4.1.34550.20.2.1.1.1.28.1.1.1 | rCMSensorIndex | Read Only | The ID of RCM sensors. From 1 ~ 13, 1 = RCM 1 , 13 = RCM 13
.1.3.6.1.4.1.34550.20.2.1.1.1.28.1.1.2 | rCMSensorLocation | Read / Write | The location of RCM sensor. Range : 1 to 16 char. Valid characters are( 0 ~ 9 ) , ( a ~ z ) , ( A ~ Z ) , ( _ ) , ( - ) and ( . )
.1.3.6.1.4.1.34550.20.2.1.1.1.28.1.1.3 | rCMSensorReading | Read Only | The reading of RCM in tenth of mA
.1.3.6.1.4.1.34550.20.2.1.1.1.28.1.1.4 | rCMSensorConnState | Read Only | The connection status of the sensor. 0 = disconnected , 1 = connected
.1.3.6.1.4.1.34550.20.2.1.1.1.28.1.1.5 | rCMSensorAlarmState | Read Only | The alarm state of the RCM sensor. 0 = normal , 1 = alarm , 2 = rising alert
.1.3.6.1.4.1.34550.20.2.1.1.1.28.1.1.6 | rCMSensorAlarmThreh | Read / Write | To set the RCM alarm threshold in tenth mA. 10 = 1.0mA , 100 = 10.0mA
.1.3.6.1.4.1.34550.20.2.1.1.1.28.1.1.7 | rCMSensorRisingAlertThreh | Read / Write | To set the RCM rising alert threshold in tenth mA. 10 = 1.0mA , 100 = 10.0mA
.1.3.6.1.4.1.34550.20.2.1.1.1.28.1.1.8 | rCMSensorLowAlertThreh | Read / Write | Reserved
.1.3.6.1.4.1.34550.20.2.2 | pduTraps | N/A
.1.3.6.1.4.1.34550.20.2.2.1 | circuitAlarmTriggered | N/A | A trap will send out in cycle when the circuit / bank level current load over the circuit amp. alarm threshold. It will stop when the cirucit level current load is below the circuit amp. alarm threshold. The time interval for one cycle is within 3 mins if 16 PDUs are connected.
.1.3.6.1.4.1.34550.20.2.2.12 | circuitBreakerTripped | N/A | A trap will send out in cycle when the circuit breaker is tripped. The time interval for one cycle is within 3 mins if 16 PDUs are connected.
.1.3.6.1.4.1.34550.20.2.2.13 | circuitBreakerRecovered | N/A | A trap will send out when the circuit breaker is resumed normal.
.1.3.6.1.4.1.34550.20.2.2.40 | tempHumiSenosorConnLost | N/A | A trap will send out in cycle when the Temp. or Temp. & humid sensor is disconnected. It will stop when the Temp. or Temp. & humid sensor is reconnected. The time interval for one cycle is within 3 mins if 16 PDUs are connected.
.1.3.6.1.4.1.34550.20.2.2.41 | tempSesnorUpperAlarmTriggered | N/A | A trap will send out in cycle when the temp. reading is over the temp. alarm threshold. It will stop when the temp. reading is below the temp. alarm threshold. The time interval for one cycle is within 3 mins if 16 PDUs are connected.
.1.3.6.1.4.1.34550.20.2.2.47 | humiSensorUpperAlarmTriggered | N/A | A trap will send out in cycle when the relative humid. reading is over the humid. alarm threshold. It will stop when the relative humid. reading is below the humid. alarm threshold. The time interval for one cycle is within 3 mins if 16 PDUs are connected.
.1.3.6.1.4.1.34550.20.2.2.53 | pduDisconnected | N/A | A trap will send out in cycle when the PDU is disconnected. It will stop when the PDU is reconnected. The time interval for one cycle is within 3 mins if 16 PDUs are connected.
.1.3.6.1.4.1.34550.20.2.2.80 | rcmSensorEventTriggered | N/A | A trap will send out in cycle when RCM reading is over the RCM alarm threshold.
.1.3.6.1.4.1.34550.20.2.2.81 | rcmSensorEventCleared | N/A | A trap will send out once when RCM reading returns below the RCM alarm threshold.
.1.3.6.1.4.1.34550.20.2.2.82 | rcmSensorConnectionLost | N/A | A trap will send out in cycle when RCM sensor loses communication.
.1.3.6.1.4.1.34550.20.2.2.83 | rcmSensorConnectionRecovered | N/A | A trap will send out once when RCM sensor resumes communication
.1.3.6.1.4.1.34550.20.4 | atsGroup | N/A | N/A
.1.3.6.1.4.1.34550.20.4.1 | atsAdmin | N/A | N/A
.1.3.6.1.4.1.34550.20.4.1.1 | atsTable | N/A | Table of ATS
.1.3.6.1.4.1.34550.20.4.1.1.1 | atsEntry | N/A | Table Entries of ATS
.1.3.6.1.4.1.34550.20.4.1.1.1.1.[16] | atsIndex | Read Only | ATS level
.1.3.6.1.4.1.34550.20.4.1.1.1.2.[16] | atsModel | Read Only | ATS Model no.
.1.3.6.1.4.1.34550.20.4.1.1.1.3.[16] | atsID | Read Only | ATS unique identifier
.1.3.6.1.4.1.34550.20.4.1.1.1.4.[16] | atsName | Read / Write | The name of ATS. Length : 1 to 16 char. Valid characters are( 0 ~ 9 ) , ( a ~ z ) , ( A ~ Z ) , ( _ ) , ( - ) and ( . )
.1.3.6.1.4.1.34550.20.4.1.1.1.5.[16] | atsLocation | Read / Write | The name of Location. Length : 1 to 16 char. Valid characters are( 0 ~ 9 ) , ( a ~ z ) , ( A ~ Z ) , ( _ ) , ( - ) and ( . )
.1.3.6.1.4.1.34550.20.4.1.1.1.6.[16] | atsInputSwitch | Read / Write | The selection of preferred source. 0 = Primary , 1 = Secondary Set : 0 = Primary , 1 = Secondary
.1.3.6.1.4.1.34550.20.4.1.1.1.7.[16] | atsFeedPrimaryStatus | Read Only | The status of Primary source. 0 = offine , 1 = online
.1.3.6.1.4.1.34550.20.4.1.1.1.8.[16] | atsFeedSecondaryStatus | Read Only | The status of Secondary source. 0 = offine , 1 = online
.1.3.6.1.4.1.34550.20.4.1.1.1.9.[16] | atsOutputFromFeed | Read Only | To show which source are supplying the electricity. 0 = Primary , 1 = Secondary
.1.3.6.1.4.1.34550.20.4.1.1.1.10.[16] | atsTotalLoadAmp | Read Only | The total current loading of the ATS in tenth of amp. 0 = 0.0A , 999 = 99.9A
.1.3.6.1.4.1.34550.20.4.1.1.1.11.[16] | atsOverLoadThreshold | Read Only | The Overload threshold of the ATS which equals to the rated input ampere. 0 = 0.0A , 999 = 99.9A The value of the overload threshold equals to 90% of the rated input ampere.
.1.3.6.1.4.1.34550.20.4.1.1.1.12.[16] | atsOverLoadStage | Read Only | The Overload stage of ATS. 0 = normal , 1 = alarm ( over the overload threshold )
.1.3.6.1.4.1.34550.20.4.1.1.1.13.[16] | atsConnection | Read Only | The connection status of ATS. 0 = disconnected , 1 = connected
.1.3.6.1.4.1.34550.20.4.2 | atsTraps | N/A
.1.3.6.1.4.1.34550.20.4.2.1 | atsOverLoadEventTriggered | N/A | A trap will send out continuously when current loading of the ATS is over the overload threshold. It will stop when the current loading is below the overload threshold.
.1.3.6.1.4.1.34550.20.4.2.2 | atsOverLoadEventCleared | N/A | A trap will send out once when the current loading returns to the value below the overload threshold.
.1.3.6.1.4.1.34550.20.4.2.3 | atsPrimaryFeedOfflineEventTriggered | N/A | A trap will send out continuously when the Primary source is offline. It will stop when the Primary source is resume normal.
.1.3.6.1.4.1.34550.20.4.2.4 | atsPrimaryFeedOfflineEventCleared | N/A | A trap will send out once when the Primary source is resume.
.1.3.6.1.4.1.34550.20.4.2.5 | atsSecondaryFeedOfflineEventTriggered | N/A | A trap will send out continuously when the Secondary source is offline. It will stop when the Secondary source is resume normal.
.1.3.6.1.4.1.34550.20.4.2.6 | atsSecondaryFeedOfflineEventCleared | N/A | A trap will send out once when the Secondary source is resume.
.1.3.6.1.4.1.34550.20.4.2.7 | atsInputSwitchEventTriggered | N/A | A trap will send out once when the preferred source is changed.
.1.3.6.1.4.1.34550.20.4.2.8 | atsOnFailAutoSwitchFeedEventTriggered | N/A | A trap will send out once when the preferred source is offline.
.1.3.6.1.4.1.34550.20.4.2.9 | atsConnectionLost | N/A | A trap will send out continuously when the ATS communication is lost. It will stop when the ATS communicatoin is resume.
.1.3.6.1.4.1.34550.20.4.2.10 | astConnectionRecovered | N/A | A trap will send out once when the ATS communication is resume.

## InfraPower
[9 empty] | OID | data source | Syntax / Object | Max-Access/Access | Status | Description
| InfraPower | [7 empty] | .1.3.6.1.4.1.34550.20 |  | DisplayString(0..32) | not-accessible | current
| -> | ipDongle | [6 empty] | .1.3.6.1.4.1.34550.20.1 |  |  | not-accessible | current
|  | -> | ipDongleAdmin | [5 empty] | .1.3.6.1.4.1.34550.20.1.1 |  |  | not-accessible | current
|  |  |  | ipdongleModel |  |  |  |  | .1.3.6.1.4.1.34550.20.1.1.1 | H03-LMGM | DisplayString(0..32) | read-only | current | The model number of the IP dongle
|  |  |  | ipdongleSerialNumber |  |  |  |  | .1.3.6.1.4.1.34550.20.1.1.2 | H01-LMGN | DisplayString(0..32) | read-only | current | The serial number of the IP dongle
|  |  |  | ipdongleHwRevision |  |  |  |  | .1.3.6.1.4.1.34550.20.1.1.3 | From IP Dognle (same as WEB GUI Firmware.php) | DisplayString(0..32) | read-only | current | The current hardware revision of the IP dongle
|  |  |  | ipdongleFwVersion |  |  |  |  | .1.3.6.1.4.1.34550.20.1.1.4 | H00-LMGV | DisplayString(0..32) | read-only | current | The current firmware version of the IP dongle
|  |  |  | ipdongleName |  |  |  |  | .1.3.6.1.4.1.34550.20.1.1.5 | H16-LMGA | DisplayString (0..32) | read-write | current | The name of the IP dongle
|  |  |  | ipdongleLocation |  |  |  |  | .1.3.6.1.4.1.34550.20.1.1.6 | H1F-LMGW | DisplayString (0..32) | read-write | current | The location of the IP dongle
|  |  |  | ipdongleGroupNumber |  |  |  |  | .1.3.6.1.4.1.34550.20.1.1.7 | 240 | INTEGER (0..240) | read-write | current | The group number of the IP dongle
|  |  |  | ipdongleMacAddress |  |  |  |  | .1.3.6.1.4.1.34550.20.1.1.8 | xx-xx-xx-xx-xx-xx | MacAddress | read-only | current | The MAC address of the IP dongle
|  |  |  | ipdongleIpAddressIpv4 |  |  |  |  | .1.3.6.1.4.1.34550.20.1.1.9 | From IP Dognle | InetAddressIPv4 | read-only | current | The current IPv4 address of the IP dongle. A value of 0.0.0.0. indicate an error or an unset option
|  |  |  | ipdongleSubnetIpv4 |  |  |  |  | .1.3.6.1.4.1.34550.20.1.1.10 | From IP Dognle | InetAddressIPv4 | read-only | current | The current IPv4 subnet of the IP dongle. A value of 0.0.0.0. indicate an error or an unset option
|  |  |  | ipdongleGatewayIpv4 |  |  |  |  | .1.3.6.1.4.1.34550.20.1.1.11 | From IP Dognle | InetAddressIPv4 | read-only | current | The current IPv4 gateway of the IP dongle. A value of 0.0.0.0. indicate an error or an unset option
Hide |  |  |  | ipdongleIpAddressIpv6 |  |  |  |  | .1.3.6.1.4.1.34550.20.1.1.12 | From IP Dognle | DisplayString | read-only | current | The current IPv6 address of the IP dongle. A value of 0.0.0.0. indicate an error or an unset option
Hide |  |  |  | ipdongleSubnetIpv6 |  |  |  |  | .1.3.6.1.4.1.34550.20.1.1.13 | From IP Dognle | DisplayString | read-only | current | The current IPv6 subnet of the IP dongle. A value of 0.0.0.0. indicate an error or an unset option
Hide |  |  |  | ipdongleGatewayIpv6 |  |  |  |  | .1.3.6.1.4.1.34550.20.1.1.14 | From IP Dognle | DisplayString | read-only | current | The current IPv6 gateway of the IP dongle. A value of 0.0.0.0. indicate an error or an unset option
|  |  |  | ipdongleNetworkMode |  |  |  |  | .1.3.6.1.4.1.34550.20.1.1.15 | From IP Dognle | INTEGER (0..4) | read-write | current | The configured network mode of the IP dongle : 0=AUTO, 1=10Mbps half-duplex, 2=10Mbps full-duplex, 3=100Mbps half-duplex, 4=100Mbps full-duplex
|  |  |  | ipdongleLinkStatus |  |  |  |  | .1.3.6.1.4.1.34550.20.1.1.16 | From IP Dognle | INTEGER (0..4) | read-only | current | The network link status of the IP dongle : 0=LinkDown, 1=10Mbps half-duplex, 2=10Mbps full-duplex, 3=100Mbps half-duplex, 4=100Mbps full-duplex
|  |  |  | ipdongleRTC |  |  |  |  | .1.3.6.1.4.1.34550.20.1.1.17 | From IP Dognle | DateAndTime | read-only | current | RTC calendar and colck, formatted to "YYYY-MM-DD HH:NN:SS.W,+0000"
new |  |  |  | objectDateTime |  |  |  |  | .1.3.6.1.4.1.34550.20.1.1.18 | From IP Dognle | DateAndTime | accessible-for-notify | current | RTC calendar and colck of the trap/notification is triggered
new |  |  |  | userName |  |  |  |  | .1.3.6.1.4.1.34550.20.1.1.19 | From IP Dognle | DisplayString | accessible-for-notify | current | Web GUI login user name
new |  |  |  | webAccessIpAddress |  |  |  |  | .1.3.6.1.4.1.34550.20.1.1.20 | From IP Dognle | InetAddressIPv4 | accessible-for-notify | current | the web access remote ipaddress
new |  |  |  | sessionID |  |  |  |  | .1.3.6.1.4.1.34550.20.1.1.21 | From IP Dognle | DisplayString | accessible-for-notify | current | the sessionID of web autherticationFailure
new |  |  |  | newUserName |  |  |  |  | .1.3.6.1.4.1.34550.20.1.1.22 | From IP Dognle | DisplayString | accessible-for-notify | current | the new web login name
new |  |  |  | modifiedUserName |  |  |  |  | .1.3.6.1.4.1.34550.20.1.1.23 | From IP Dognle | DisplayString | accessible-for-notify | current | tthe updated web login name
new |  |  |  | targetUserName |  |  |  |  | .1.3.6.1.4.1.34550.20.1.1.24 | From IP Dognle | DisplayString | accessible-for-notify | current | he web login name is going to delete / change password
new |  |  |  | ipdonglePDURegistration |  |  |  |  | .1.3.6.1.4.1.34550.20.1.1.25 | same as "Search" button on WEB GUI, will update modelPrPifile | DisplayString | read-write | current | Register the cascade status of PDU(s) connection to IP dongle for SNMP monitoring, re-registration are required when PDU is added or removed from the cascade chain. Read: FFFF=16xPDU, 0000=zero PDU; write:same as WEB GUI seach button.
|  | -> | ipDongleTraps | [5 empty] | .1.3.6.1.4.1.34550.20.1.2 |  |  | not-accessible | current
rename |  |  |  | webLogin |  |  |  |  | .1.3.6.1.4.1.34550.20.1.2.1 |  | objectDateTime, userName, webAccessIpAddress | read-only | current | A user logged in (success)
rename |  |  |  | webLogout |  |  |  |  | .1.3.6.1.4.1.34550.20.1.2.2 |  | objectDateTime, userName, webAccessIpAddress | read-only | current | A user logged out (success)
rename |  |  |  | webAutherticationFailure |  |  |  |  | .1.3.6.1.4.1.34550.20.1.2.3 |  | objectDateTime, userName, webAccessIpAddress | read-only | current | A user authentication attempt failed
rename |  |  |  | webSessionTimeout |  |  |  |  | .1.3.6.1.4.1.34550.20.1.2.4 |  | objectDateTime, userName, webAccessIpAddress, sessionID | read-only | current | A user timed out from the device
hide |  |  |  | webLoginAdded |  |  |  |  | .1.3.6.1.4.1.34550.20.1.2.5 |  | objectDateTime, userName, webAccessIpAddress, newUserName | read-only | current | A user was added to system
rename |  |  |  | webLoginModified |  |  |  |  | .1.3.6.1.4.1.34550.20.1.2.6 |  | objectDateTime, userName, webAccessIpAddress, modifiedUserName | read-only | current | A user account was modified
hide |  |  |  | webLoginDeleted |  |  |  |  | .1.3.6.1.4.1.34550.20.1.2.7 |  | objectDateTime, userName, webAccessIpAddress, targetUserName | read-only | current | A user account was modified
rename |  |  |  | webPasswordChange |  |  |  |  | .1.3.6.1.4.1.34550.20.1.2.8 |  | objectDateTime, userName, webAccessIpAddress, targetUserName | read-only | current | A user was deleted from the system
rename |  |  |  | ipDongleReboot |  |  |  |  | .1.3.6.1.4.1.34550.20.1.2.9 |  | objectDateTime, userName, webAccessIpAddress | read-only | current | The reboot process has started
rename |  |  |  | ipDongleBootUpOk |  |  |  |  | .1.3.6.1.4.1.34550.20.1.2.10 |  | objectDateTime | read-only | current | The bootup process has finished succssfully
|  | pduGroup | [6 empty] | .1.3.6.1.4.1.34550.20.2 |  |  | not-accessible | current
|  |  | pduTable | [5 empty] | .1.3.6.1.4.1.34550.20.2.1 | Table of PDU |  | not-accessible | current
|  |  |  | pduEntry |  |  |  |  | .1.3.6.1.4.1.34550.20.2.1.1 | Table Entry of PDU Level [1..16] |  | not-accessible | current
[5 empty] | pduAdmin |  |  |  | .1.3.6.1.4.1.34550.20.2.1.1.1 |  |  | not-accessible | current
[6 empty] | pduIndex |  |  | .1.3.6.1.4.1.34550.20.2.1.1.1.1.[1..16] | [aa], RS485 address of Meter = Level | INTEGER (1..16) | read-only | current | The level of this PDU. (RS485 address 00= index 1, 01=index 2 … 15=index 16)
[6 empty] | pduModel |  |  | .1.3.6.1.4.1.34550.20.2.1.1.1.2.[1..16] | H1A-PHGL.[mmmm] | DisplayString(0..32) | read-only | current | The model number of this PDU.
[6 empty] | pduSerialNo |  |  | .1.3.6.1.4.1.34550.20.2.1.1.1.3.[1..16] | H37-PHPY.[serialno] | DisplayString(0..16) | read-only | current | The serial number of this PDU.
[6 empty] | pduHwRevision |  |  | .1.3.6.1.4.1.34550.20.2.1.1.1.4.[1..16] | H4F-PHRA.[n][ssss], [n]=9 | DisplayString(0..16) | read-only | current | The hardware revision of this PDU.
[6 empty] | pduFwVersion |  |  | .1.3.6.1.4.1.34550.20.2.1.1.1.5.[1..16] | H37-PHPY.[firmware] | DisplayString(0..16) | read-only | current | The firmware version of this PDU
[6 empty] | pduName |  |  | .1.3.6.1.4.1.34550.20.2.1.1.1.6.[1..16] | H15-PHGC.[ssss] | DisplayString(0..16) | read-write | current | The name of this PDU.
[6 empty] | pduLocation |  |  | .1.3.6.1.4.1.34550.20.2.1.1.1.7.[1..16] | H4D-PHCL.[ssss] | DisplayString(0..16) | read-write | current | The location of this PDU.
[6 empty] | pduGroupNumber |  |  | .1.3.6.1.4.1.34550.20.2.1.1.1.8.[1..16] | H44-PHGG.[ss] | DisplayString(0..16) | read-write | current | The group number of this PDU.
[6 empty] | pduType |  |  | .1.3.6.1.4.1.34550.20.2.1.1.1.9.[1..16] | H4F-PHRA.[n][ssss], [n]=0, Byte 1 | DisplayString(0..16) | read-only | current | The capabilities of this PDU, (1)=monitored, (2)=switched, (3)=outlet monitored, (4) =outlet monitored and switched
[6 empty] | pduInletRatedAmp |  |  | .1.3.6.1.4.1.34550.20.2.1.1.1.10.[1..16] | H18-PHMA0[sss] + H18-PHMA1[sss] | DisplayString(0..3)* | read-only | current | The input current rating of this PDU in tenths of Amps
[6 empty] | pduInletRatedVoltage |  |  | .1.3.6.1.4.1.34550.20.2.1.1.1.11.[1..16] | H4F-PHRA.[n][ssss], [n]=0, Byte 2-5 | DisplayString(0..4)* | read-only | current | The rated voltage of this PDU in tenths of Volts
[6 empty] | pduMainStatus |  |  | .1.3.6.1.4.1.34550.20.2.1.1.1.12.[1..16] | 0=Normal(both circuits are normal), 1=Alarm | INTEGER (0 … 1) | read-only | current | The status of this PDU, (0)=Normal, (1)=Alarm
[6 empty] | pduMainLoadVoltage |  |  | .1.3.6.1.4.1.34550.20.2.1.1.1.13.[1..16] | H36-PHPX.[acvoltage] | DisplayString(0..4)* | read-only | current | The voltage measured for this PDU in tenths of Volts
[6 empty] | pduMainLoadAmp |  |  | .1.3.6.1.4.1.34550.20.2.1.1.1.14.[1..16] | H36-PHPX.[cirA_current] + .[cirB_current] | DisplayString(0..3)* | read-only | current | The load measured for this PDU in tenths of Amps
[6 empty] | pduMainLoadEngergy |  |  | .1.3.6.1.4.1.34550.20.2.1.1.1.15.[1..16] | P=Voltage * Current (CirA +CirB) | DisplayString(0..7) | read-only | current | The value of the energy consumption for this PDU in hundredth of kilowatt-hours
[6 empty] | pduMainPowerFactor |  |  | .1.3.6.1.4.1.34550.20.2.1.1.1.16.[1..16] | H36-PHPX.[powerfactor] | DisplayString(0..3) | read-only | current | The value of the power factor for this PDU in hundredths, "000" ~ "100", in foimat of "A.BB", where A is digits before decimal place, B is the digits after decimal place.
[6 empty] | pduMainActivePower |  |  | .1.3.6.1.4.1.34550.20.2.1.1.1.17.[1..16] | H36-PHPX.[activepower cir1 + cir2 ] | DisplayString(0..7) | read-only | current | The value of the active power consumption for this PDU in hundredth of kW, "0000000" ~ "9999999", in foimat of "AAAAA.BB", where A is digits before decimal place, B is the digits after decimal place.
[6 empty] | pduMainApparentPower |  |  | .1.3.6.1.4.1.34550.20.2.1.1.1.18.[1..16] | H36-PHPX.[activepower cir1 + cir2 ] | DisplayString(0..7) | read-only | current | The value of the apparent power consumption for this PDU in hundredth of kVA, "0000000" ~ "9999999", in foimat of "AAAAA.BB", where A is digits before decimal place, B is the digits after decimal place.
[6 empty] | pduMainCumulativeEnergy |  |  | .1.3.6.1.4.1.34550.20.2.1.1.1.19.[1..16] | H36-PHPX (CirA + CirB) | DisplayString(21) | read-only | current | The accumulated energy of this PDU in hundredth of kilowatt-hours
[6 empty] | pduRealTimeClock |  |  | .1.3.6.1.4.1.34550.20.2.1.1.1.20.[1..16] | H36-PHPX.[datetime] | DisplayString(0..14) | read-only | current | The real time clock & calendar. Formatted to "YYYY-MM-DD HH:NN:SS.W,+0000"
[6 empty] | pduAlarmBuzzerPause |  |  | .1.3.6.1.4.1.34550.20.2.1.1.1.21.[1..16] | H0A-PHRT.[nnn] | INTEGER (0..999) | read-write | current | Pause buzzer output when alarm stage is triggered. Pause duration can be specified from 0 to 999 minutes. Will be cleared after pause timer count to 0.
NEW | [5 empty] | pduConnState |  |  | .1.3.6.1.4.1.34550.20.2.1.1.1.22.[1..16] | Connection state of the PDU | INTEGER (0 … 1) | read-only | current | 0=Disconnected, 1=Connected
NEW | [5 empty] | pduActivation |  |  | .1.3.6.1.4.1.34550.20.2.1.1.1.23.[1..16] | change the deviceprofile | INTEGER (0 … 1) | read-write | current | 0=Deactivated the connection monitroing (this pdu connectivity =0), 1=Actvated the connection monitoring (this pdu connectivity =1)
[6 empty] | circuits |  |  | .1.3.6.1.4.1.34550.20.2.1.1.1.24 |  |  | not-accessible | current
[7 empty] | circuitTable |  | .1.3.6.1.4.1.34550.20.2.1.1.1.24.1 | Table of Circuits |  | not-accessible | current
[8 empty] | circuitTablEntry | .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1 | Table Entry of Circuits [1..2] |  | not-accessible | current
[8 empty] | circuitIndex | .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.1.[1..16].[1..2] | H1A-PHGL | INTEGER (1..2) | read-only | current | Circuit ID, 1=Circuit A, 2=Circuit B
[8 empty] | circuitRatedAmp | .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.2.[1..16].[1..2] | H18-PHMA0[sss] | DisplayString(0..3)* | read-only | current | The input current rating of this circuit in Amps
[8 empty] | circuitRatedVoltage | .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.3.[1..16].[1..2] | H4F-PHRA.[n][ssss], [n]=1 byte 1~4 for circuitIndex=1; H4F-PHRA.[n][ssss], [n]=1 byte 5~8 for circuitIndex=2 | DisplayString(0..4)* | read-only | current | The rated voltage of this circuit in tenths of Amps
[8 empty] | circuitName | .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.4.[1..16].[1..2] | H4F-PHRA.[n][ssss], [n]=2 for circuitIndex=1; H4F-PHRA.[n][ssss], [n]=3 for circuitIndex=2 | DisplayString(16)* | read-write | current | The name of this circuit, e.g. circuit index 1=Circuit A, circuit index 2=Circuit B
[8 empty] | circuitState | .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.5.[1..16].[1..2] | H36-PHPX | INTEGER(0..4) | read-only | current | The status of this circuit, 0=Normal, 1=Alarm, 2=Alert, 3=Low , 4=not exist
[8 empty] | circuitLoadVoltage | .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.6.[1..16].[1..2] | H36-PHPX.[ac_voltage] | DisplayString(0..4)* | read-only | current | The volatge measured for this circuit in tenths of Volts
[8 empty] | circuitLoadAmp | .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.7.[1..16].[1..2] | H36-PHPX.[cirA_current] | DisplayString(0..3)* | read-only | current | The load measured for this circuit in tenths of Amps
[8 empty] | circuitEnergy | .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.8.[1..16].[1..2] | P=VI | DisplayString(0..7) | read-only | current | The value of the energy consumption for this circuit in hundredth of kilowatt-hours
[8 empty] | circuitPowerFactor | .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.9.[1..16].[1..2] | H36-PHPX.[power_factor] | DisplayString(0..3) | read-only | current | The value of the power factor for this circuit in hundredths
[8 empty] | circuitActivePower | .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.10.[1..16].[1..2] | H36-PHPX | DisplayString(0..7) | read-only | current | The value of the active power consumption for this circuit in hundredth of kW
[8 empty] | circuitApparentPower | .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.11.[1..16].[1..2] | H36-PHPX | DisplayString(0..7) | read-only | current | The value of the apparent power consumption for this circuit in hundredth of kVA
[8 empty] | circuitLoadPeakAmp | .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.12.[1..16].[1..2] | H36-PHPX | DisplayString(16) | read-only | current | The value of the peak current of this circuit in tenths of Amps (aab) with time stamp in < yymmddhhnnss@aab > format
[8 empty] | circuitCumulativeEnergy | .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.13.[1..16].[1..2] | H36-PHPX | DisplayString(21) | read-only | current | The accumulated energy of this circuit in hundredth of kilowatt-hours
[8 empty] | circuitLoadPeakAmpReset | .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.14.[1..16].[1..2] | H55-PHSS | DisplayString(1) | write-only | current | Reset the peak current of the circuit to zero, 1=confirm reset
Rename | [7 empty] | circuitBreakerStateCopy | .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.15.[1..16].[1..2] | H36-PHPX | INTEGER(0..1) | read-only | current | The value for the circuit breaker state, 0=connected, 1= tripped
[8 empty] | circuitLoadAmpAlarmThresh | .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.16.[1..16].[1..2] | H37-PHPY | DisplayString(0..3) | read-write | current | The upper alarm current threshold of this circuit in tenths of Amps.
[8 empty] | circuitLoadAmpAlertThresh | .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.17.[1..16].[1..2] | H37-PHPY | DisplayString(0..3) | read-write | current | The upper alert current threshold of this circuit in tenths of Amps.
[8 empty] | circuitLoadAmpLowAlertThresh | .1.3.6.1.4.1.34550.20.2.1.1.1.24.1.1.18.[1..16].[1..2] | H37-PHPY | DisplayString(0..3) | read-write | current | The lower alert current threshold of this circuit in tenths of Amps.
[6 empty] | circuitBreakers |  |  | .1.3.6.1.4.1.34550.20.2.1.1.1.25 |  |  | not-accessible | current
[7 empty] | circuitBreakerTable |  | .1.3.6.1.4.1.34550.20.2.1.1.1.25.1 | Table of Breakers |  | not-accessible | current
[8 empty] | circuitBreakerTableEntry | .1.3.6.1.4.1.34550.20.2.1.1.1.25.1.1 | Table Entry of Breakers [1..2] |  | not-accessible | current
[8 empty] | circuitBreakerIndex | .1.3.6.1.4.1.34550.20.2.1.1.1.25.1.1.1.[1..16].[1..2] | 1=Breaker for Circuit A, 2=Breaker for Circuit B | INTEGER (1..2) | read-only | current | Circuit Breaker ID, value (1)=circuit breaker A, (2)=circuit breaker B,
[8 empty] | circuitBreakerRatedAmp | .1.3.6.1.4.1.34550.20.2.1.1.1.25.1.1.2.[1..16].[1..2] | H4F-PHRA.[n][ssss], [n]=4 byte 1~4 for circuitBreakerIndex=1; H4F-PHRA.[n][ssss], [n]=4 byte 5~8 for circuitBreakerIndex=2 | DisplayString(0..3)* | read-only | current | The current rating of this circuit breaker in tenths of Amps.
[8 empty] | circuitBreakerName | .1.3.6.1.4.1.34550.20.2.1.1.1.25.1.1.3.[1..16].[1..2] | H4F-PHRA.[n][ssss], [n]=5 for circuitBreakerIndex=1; H4F-PHRA.[n][ssss], [n]=6 for circuitBreakerIndex=2 | DisplayString(16) | read-write | current | The name of this circuit breaker
[8 empty] | circuitBreakerState | .1.3.6.1.4.1.34550.20.2.1.1.1.25.1.1.4.[1..16].[1..2] | H36-PHPX | INTEGER(0..1) | read-only | current | The value for the circuit breaker state, 0=connected, 1= tripped
[6 empty] | outlets |  |  | .1.3.6.1.4.1.34550.20.2.1.1.1.26 |  |  | not-accessible | current
[7 empty] | stdOutletTable |  | .1.3.6.1.4.1.34550.20.2.1.1.1.26.1 | Table of Outlets |  | not-accessible | current
[8 empty] | stdOutletTableEntry | .1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1 | Table Entry of Outlets [1..48] |  | not-accessible | current
[8 empty] | stdOutletIndex | .1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.1.[1..16].[1..48] | H5E-PHQG | INTEGER(1..48) | read-only | current | The value of a unique number for this outlet
[8 empty] | stdOutletCircuit | .1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.2.[1..16].[1..48] | H1A-PHGL | DisplayString(1..2) | read-only | current | The value of the circuit for this outlet, (1)= Circuit A, (2)=Circuit B
[8 empty] | stdOutletType | .1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.3.[1..16].[1..48] | H1A-PHGL | DisplayString(0..16) | read-only | current | The value of outlet type for this outlet, (1)=IEC C13, (2)=NEMA 5-20, (3)=BS1363, (4)=Schuko, (5)=French, (6)=AS 3112
[8 empty] | stdOutletName | .1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.4.[1..16].[1..48] | H11-PHGO | DisplayString(0..16) | read-write | current | The name of this outlet.
[8 empty] | stdOutletRatedAmp | .1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.5.[1..16].[1..48] | H18-PHMA0[sss] same as CircuitRatedAmp | DisplayString(0..3)* | read-only | current | The current rating of this outlet in tenths of Amps.
[8 empty] | stdOutletRatedVoltage | .1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.6.[1..16].[1..48] | same as circuitRatedVoltage | DisplayString(0..4)* | read-only | current | The rated voltage of this outlet in tenths of Volts.
[8 empty] | stdOutletPowerStatus | .1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.7.[1..16].[1..48] | H36-PHPX | INTEGER(0..1) | read-only | current | The value of the power state for this outlets, (0) = OFF, (1) = ON
[8 empty] | stdOutletAlarmState | .1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.8.[1..16].[1..48] | H36-PHPX | INTEGER(0..4) | read-only | current | The value of the alarm state for this outlets, (0) = normal, (1) = alarm, (2)=alert, (3) = low alert, (4) = no exist
[8 empty] | stdOutletLoadAmp | .1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.9.[1..16].[1..48] | H49-PHOX | DisplayString(0..3)* | read-only | current | The load measured for this outlet in tenths of Amps
[8 empty] | stdOutletEnergy | .1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.10.[1..16].[1..48] | H49-PHOX | DisplayString(0..7) | read-only | current | The value of the energy consumption for this outlet in kilowatt-hours
[8 empty] | stdOutletPeakAmp | .1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.11.[1..16].[1..48] | H49-PHOX | DisplayString(16) | read-only | current | The value of the peak current of this outlet in tenths of Amps (aab) with time stamp in < yymmddhhnnss@aab > format
[8 empty] | stdOutletCumulativeEnergy | .1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.12.[1..16].[1..48] | H49-PHOX | DisplayString(21) | read-only | current | The accumulated energy of this outlet in hundredth of kilowatt-hours with time stapm in < yymmddhhnnss@caaaaabb > format
[8 empty] | stdOutletLoadAmpAlarmThresh | .1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.13.[1..16].[1..48] | H4A-PHOY | DisplayString(0..3) | read-write | current | The upper alarm current threshold of this outlet in tenths of Amps.
[8 empty] | stdOutletLoadAmpAlertThresh | .1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.14.[1..16].[1..48] | H4A-PHOY | DisplayString(0..3) | read-write | current | The upper alert current threshold of this outlet in tenths of Amps.
[8 empty] | stdOutletLoadAmpLowAlertThresh | .1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.15.[1..16].[1..48] | H4A-PHOY | DisplayString(0..3) | read-write | current | The lower alert current threshold of this outlet in tenths of Amps.
[8 empty] | stdOutletPeakAmpReset | .1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.16.[1..16].[1..48] | H4B-PHOR | DisplayString(1) | write-only | current | Reset the peak current of this outlet to zero. 1=confirm reset
[8 empty] | stdOutletCumulativeEnergyReset | .1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.17.[1..16].[1..48] | H3E-PHOC | DisplayString(1) | write-only | current | Reset the cumulative energy consumption counter of this outlet to zero, 1=confirm reset
[8 empty] | stdOutletPowerUpSequenceDelay | .1.3.6.1.4.1.34550.20.2.1.1.1.26.1.1.18.[1..16].[1..48] | H3F-PHOO | INTEGER(0..9) | read-write | current | The power up sequence delay of this outlet in seconds
[7 empty] | c19OutletTable |  | .1.3.6.1.4.1.34550.20.2.1.1.1.26.2 | Table of Outlets |  | not-accessible | current
[8 empty] | c19OutletTableEntry | .1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1 | Table Entry of Outlets [1..48] |  | not-accessible | current
[8 empty] | c19OutletIndex | .1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.1.[1..16].[1..48] | H5E-PHQG | INTEGER(1..48) | read-only | current | The value of a unique number for this outlet
[8 empty] | c19OutletCircuit | .1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.2.[1..16].[1..48] | H1A-PHGL | DisplayString(1..2) | read-only | current | The value of the circuit for this outlet, (1)= Circuit A, (2)=Circuit B
[8 empty] | c19OutletType | .1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.3.[1..16].[1..48] | H1A-PHGL | DisplayString(0..16) | read-only | current | The value of outlet type for this outlet, (1)=IEC C13, (2)=IEC C19, (3)=BS1363, (4)=NEMA 5-20R, (5)=CEE7
[8 empty] | c19OutletName | .1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.4.[1..16].[1..48] | H11-PHGO | DisplayString(0..16) | read-write | current | The name of this outlet.
[8 empty] | c19OutletRatedAmp | .1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.5.[1..16].[1..48] | H18-PHMA0[sss] same as CircuitRatedAmp | DisplayString(0..3)* | read-only | current | The input current rating of this outlet in tenths of Amps
[8 empty] | c19OutletRatedVoltage | .1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.6.[1..16].[1..48] | same as circuitRatedVoltage | DisplayString(0..4)* | read-only | current | The rated voltage of this outlet in tenths of Volts
[8 empty] | c19OutletPowerStatus | .1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.7.[1..16].[1..48] | H36-PHPX | INTEGER(0..1) | read-only | current | The value of the power state for this outlets, (0) = OFF, (1) = ON
[8 empty] | c19OutletAlarmState | .1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.8.[1..16].[1..48] | H36-PHPX | INTEGER(0..4) | read-only | current | The value of the alarm state for this outlets, (0) = normal, (1) = alarm, (2)=alert, (3) = low alert, (4) = no exist
[8 empty] | c19OutletLoadAmp | .1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.9.[1..16].[1..48] | H49-PHOX | DisplayString(0..3)* | read-only | current | The load measured for this outlet in tenths of Amps
[8 empty] | c19OutletEnergy | .1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.10.[1..16].[1..48] | H49-PHOX | DisplayString(0..7) | read-only | current | The value of the energy consumption for this outlet in hundredth of kilowatt-hours
[8 empty] | c19OutletPeakAmp | .1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.11.[1..16].[1..48] | H49-PHOX | DisplayString(16) | read-only | current | The value of the peak current of this outlet in tenths of Amps (aab) with time stamp in < yymmddhhnnss@aab > format
[8 empty] | c19OutletCumulativeEnergy | .1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.12.[1..16].[1..48] | H49-PHOX | DisplayString(21) | read-only | current | The accumulated energy of this outlet in hundredth of kilowatt-hours with time stapm in < yymmddhhnnss@caaaaabb > format
[8 empty] | c19OutletLoadAmpAlarmThresh | .1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.13.[1..16].[1..48] | H4A-PHOY | DisplayString(0..3) | read-write | current | The upper alarm current threshold of this outlet in tenths of Amps.
[8 empty] | c19OutletLoadAmpAlertThresh | .1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.14.[1..16].[1..48] | H4A-PHOY | DisplayString(0..3) | read-write | current | The upper alert current threshold of this outlet in tenths of Amps.
[8 empty] | c19OutletLoadAmpLowAlertThresh | .1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.15.[1..16].[1..48] | H4A-PHOY | DisplayString(0..3) | read-write | current | The lower alert current threshold of this outlet in tenths of Amps.
[8 empty] | c19OutletPeakAmpReset | .1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.16.[1..16].[1..48] | H4B-PHOR | DisplayString(1) | write-only | current | Reset the peak current of this outlet to zero. 1=confirm reset
[8 empty] | c19OutletCumulativeEnergyReset | .1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.17.[1..16].[1..48] | H3E-PHOC | DisplayString(1) | write-only | current | Reset the cumulative energy consumption counter of this outlet to zero, 1=confirm reset
[8 empty] | c19OutletPowerUpSequenceDelay | .1.3.6.1.4.1.34550.20.2.1.1.1.26.2.1.18.[1..16].[1..48] | H3F-PHOO | INTEGER(0..9) | read-write | current | The power up sequence delay of this outlet in seconds
rename | [5 empty] | THSensors |  |  | .1.3.6.1.4.1.34550.20.2.1.1.1.27 |  |  | not-accessible | current
rename | [6 empty] | THsensorTable |  | .1.3.6.1.4.1.34550.20.2.1.1.1.27.1 | Table of Sensors |  | not-accessible | current
rename | [7 empty] | THsensorTableEntry | .1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1 | Table Entry of Sensors [1..2] |  | not-accessible | current
rename | [7 empty] | THSensorIndex | .1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.1.[1..16].[1..2] | 1 | INTEGER (1..2) | read-only | current | The id of the sensor.1=TH1, 2=TH2
rename | [7 empty] | THSensorName | .1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.2.[1..16].[1..2] | H4F-PHRA.[n][ssss], [n]=7 for tempHumiSensorIndex=1; H4F-PHRA.[n][ssss], [n]=8 for tempHumiSensorIndex=2 | DisplayString(0..16) | read-write | current | The name assigned to the sensor.
rename | [7 empty] | THSensorLocation | .1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.3.[1..16].[1..2] | H4D-PHCL | DisplayString(0..16) | read-write | current | The location of the sensor.
rename | [7 empty] | THSensorType | .1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.4.[1..16].[1..2] | H36-PHPX | DisplayString(0..16) | read-only | current | The sensor type. (1) = Temperature sensor, (2) = Temperature-Humidity sensor
rename | [7 empty] | THSensorConnState | .1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.5.[1..16].[1..2] | H36-PHPX | INTEGER (0..1) | read-only | current | 0=connected, 1=disconnected
rename | [7 empty] | THSensorAlarmState | .1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.6.[1..16].[1..2] | H36-PHPX | INTEGER (0..99) | read-only | current | 2 digit, first digit = temperature status & second digit = humidity status 0= normal, 1= high alarm, 2= low alarm
[8 empty] | tempSensorValue | .1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.7.[1..16].[1..2] | H36-PHPX | INTEGER (0..999) | read-only | current | The temperature measured in tenths of degree Celsius
[8 empty] | tempSensorValueStr | .1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.8.[1..16].[1..2] | H36-PHPX | DisplayString(0..4) | read-only | current | The temperature reading, in degrees celsius, shown as a string (or empty string if it is not plugged into a port).
[8 empty] | tempSensorUpperAlarmThresh | .1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.9.[1..16].[1..2] | H37-PHPY | DisplayString(0..4) | read-wrtie | current | The value of the upper temperature warning threshold in tenths of degree Celsius
[8 empty] | tempSensorLowerAlarmThresh | .1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.10.[1..16].[1..2] | H37-PHPY | DisplayString(0..4) | read-write | current | The value of the lower temperature warning threshold in tenths of degree Celsius
[8 empty] | humiSensorValue | .1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.11.[1..16].[1..2] | H36-PHPX | INTEGER (0..999) | read-only | current | The relative humidity measured by the sensor in percent.
[8 empty] | humiSensorValueStr | .1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.12.[1..16].[1..2] | H36-PHPX | DisplayString(0..3) | read-only | current | The relative humidity measured by the sensor in percent, shown as a string (or empty string if it is not plugged into a port).
[8 empty] | humiSensorUpperAlarmThresh | .1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.13.[1..16].[1..2] | H37-PHPY | DisplayString(0..3) | read-write | current | The value of the upper relative humidity warning threshold in percent.
[8 empty] | humiSensorLowerAlarmThresh | .1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.14.[1..16].[1..2] | H37-PHPY | DisplayString(0..3) | read-write | current | The value of the lower relative humidity warning threshold in percent.
NEW | [7 empty] | THSensorActivation | .1.3.6.1.4.1.34550.20.2.1.1.1.27.1.1.15.[1..16].[1..2] | IF 0, then H32-PHTC.[w]="1", IF 1, the H32-PHTC.[w]="0" | INTEGER (0..1) | read-write | current | 0=Deactivated. 1=Actvated
|  |  | pduTraps | [5 empty] | .1.3.6.1.4.1.34550.20.2.2
|  |  |  | circuitAlarmTriggered |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.1 |  | pduIndex, pduName, pduLocation, circuitIndex, circuitName, circuitState,circuitLoadAmp |  |  | The circuit alarm of this PDU triggered
|  |  |  | circuitAlarmCleared |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.2 |  | pduIndex, pduName, pduLocation, circuitIndex, circuitName, circuitState,circuitLoadAmp |  |  | The circuit alarm of this PDU cleared
|  |  |  | circuitAlarmThreshChanged |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.3 |  | pduIndex, pduName, pduLocation, circuitIndex, circuitName, circuitLoadAmpAlarmThresh |  |  | The circuit alarm of this PDU threshold changed
Hide |  |  |  | circuitAlertTriggered |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.4 |  | pduIndex, pduName, pduLocation, circuitIndex, circuitName, circuitState,circuitLoadAmp |  |  | The circuit alert of this PDU triggered
Hide |  |  |  | circuitAlertCleared |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.5 |  | pduIndex, pduName, pduLocation, circuitIndex, circuitName, circuitState,circuitLoadAmp |  |  | The circuit alert of this PDU cleared
Hide |  |  |  | circuitAlertThreshChanged |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.6 |  | pduIndex, pduName, pduLocation, circuitIndex, circuitName, circuitLoadAmpAlertThresh |  |  | The circuit alert threshold of this PDU changed
|  |  |  | circuitLowAlertTriggered |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.7 |  | pduIndex, pduName, pduLocation, circuitIndex, circuitName, circuitState,circuitLoadAmp |  |  | The circuit low alert of this PDU triggered
|  |  |  | circuitLowAlrerCleared |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.8 |  | pduIndex, pduName, pduLocation, circuitIndex, circuitName, circuitState,circuitLoadAmp |  |  | The circuit low alert of this PDU cleared
|  |  |  | circuitLowAlertThreshChanged |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.9 |  | pduIndex, pduName, pduLocation, circuitIndex, circuitName, circuitLoadAmpLowAlertThresh |  |  | The circuit low alert threshold of this PDU changed
Hide |  |  |  | circuitPeakAmpChanged |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.10 |  | pduIndex, pduName, pduLocation, circuitIndex, circuitName, circuitLoadPeakAmp |  |  | The circuit peak Amp of this PDU changed
Hide |  |  |  | circuitPeakAmpReseted |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.11 |  | pduIndex, pduName, pduLocation, circuitIndex, circuitName, circuitLoadPeakAmp |  |  | The circuit peak Amp of this PDU reset
|  |  |  | circuitBreakerTripped |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.12 |  | pduIndex, pduName, pduLocation, circuitBreakerIndex, circuitBreakerName, circuitBreakerState |  |  | The circuit breaker of this PDU tripped
|  |  |  | circuitBreakerRecovered |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.13 |  | pduIndex, pduName, pduLocation, circuitBreakerIndex, circuitBreakerName, circuitBreakerState |  |  | The circuit breaker of this PDU recovered
|  |  |  | stdOutletControl |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.14 |  | pduIndex, pduName, pduLocation, stdOutletIndex, stdOutletName, stdOutletPowerStatus |  |  | The standard outlet of this PDU switched
|  |  |  | stdOutletAlarmTriggered |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.15 |  | pduIndex, pduName, pduLocation, stdOutletIndex, stdOutletName, stdOutletAlarmState, stdOutletLoadAmp |  |  | The standard outlet alarm of this PDU triggered
|  |  |  | stdOutletAlarmCleared |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.16 |  | pduIndex, pduName, pduLocation, stdOutletIndex, stdOutletName, stdOutletAlarmState, stdOutletLoadAmp |  |  | The standard outlet alarm of this PDU cleared
|  |  |  | stdOutletAlarmThreshChanged |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.17 |  | pduIndex, pduName, pduLocation, stdOutletIndex, stdOutletName, stdOutletLoadAmpAlarmThresh |  |  | The standard outlet alarm of this PDU threshold changed
Hide |  |  |  | stdOutletAlertTriggered |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.18 |  | pduIndex, pduName, pduLocation, stdOutletIndex, stdOutletName, stdOutletAlarmState, stdOutletLoadAmp |  |  | The standard outlet alert of this PDU triggered
Hide |  |  |  | stdOutletAlertCleared |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.19 |  | pduIndex, pduName, pduLocation, stdOutletIndex, stdOutletName, stdOutletAlarmState, stdOutletLoadAmp |  |  | The standard outlet alert of this PDU cleared
Hide |  |  |  | stdOutletAlertThreshChanged |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.20 |  | pduIndex, pduName, pduLocation, stdOutletIndex, stdOutletName, stdOutletLoadAmpAlertThresh |  |  | The standard outlet alert of this PDU threshold changed
|  |  |  | stdOutletLowAlertTriggered |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.21 |  | pduIndex, pduName, pduLocation, stdOutletIndex, stdOutletName, stdOutletAlarmState, stdOutletLoadAmp |  |  | The standard outlet low alert of this PDU triggered
|  |  |  | stdOutletLowAlertCleared |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.22 |  | pduIndex, pduName, pduLocation, stdOutletIndex, stdOutletName, stdOutletAlarmState, stdOutletLoadAmp |  |  | The standard outlet low alert of this PDU cleared
|  |  |  | stdOutletLowAlertThreshChanged |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.23 |  | pduIndex, pduName, pduLocation, stdOutletIndex, stdOutletName, stdOutletLoadAmpLowAlertThresh |  |  | The standard outlet low alert of this PDU threshold changed
Hide |  |  |  | stdOutletPeakAmpChanged |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.24 |  | pduIndex, pduName, pduLocation, stdOutletIndex, stdOutletName, stdOutletPeakAmp |  |  | The standard outlet peak Amp of this PDU changed
Hide |  |  |  | stdOutletPeakAmpReseted |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.25 |  | pduIndex, pduName, pduLocation, stdOutletIndex, stdOutletName, stdOutletPeakAmp |  |  | The standard outlet peak Amp of this PDU reset
|  |  |  | stdOutletCumulativeEnergyReseted |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.26 |  | pduIndex, pduName, pduLocation, stdOutletIndex, stdOutletName, stdOutletCumulativeEnergy |  |  | The standard outlet cumulative energy of this PDU reset
|  |  |  | c19OutletControl |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.27 |  | pduIndex, pduName, pduLocation, c19OutletIndex, c19OutletName, c19OutletPowerStatus |  |  | The C19 outlet of this PDU switched
|  |  |  | c19OutletAlarmTriggered |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.28 |  | pduIndex, pduName, pduLocation, c19OutletIndex, c19OutletName, c19OutletAlarmState, c19OutletLoadAmp |  |  | The C19 outlet alarm of this PDU triggered
|  |  |  | c19OutletAlarmCleared |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.29 |  | pduIndex, pduName, pduLocation, c19OutletIndex, c19OutletName, c19OutletAlarmState, c19OutletLoadAmp |  |  | The C19 outlet alarm of this PDU cleared
|  |  |  | c19OutletAlarmThreshChanged |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.30 |  | pduIndex, pduName, pduLocation, c19OutletIndex, c19OutletName, c19OutletLoadAmpAlarmThresh |  |  | The C19 outlet alarm threshold of this PDU changed
Hide |  |  |  | c19OutletAlertTriggered |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.31 |  | pduIndex, pduName, pduLocation, c19OutletIndex, c19OutletName, c19OutletAlarmState, c19OutletLoadAmp |  |  | The C19 outlet alert of this PDU triggered
Hide |  |  |  | c19OutletAlertCleared |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.32 |  | pduIndex, pduName, pduLocation, c19OutletIndex, c19OutletName, c19OutletAlarmState, c19OutletLoadAmp |  |  | The C19 outlet alert of this PDU cleared
Hide |  |  |  | c19OutletAlertThreshChanged |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.33 |  | pduIndex, pduName, pduLocation, c19OutletIndex, c19OutletName, c19OutletLoadAmpAlertThresh |  |  | The C19 outlet alert threshold of this PDU changed
|  |  |  | c19OutletLowAlertTriggered |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.34 |  | pduIndex, pduName, pduLocation, c19OutletIndex, c19OutletName, c19OutletAlarmState, c19OutletLoadAmp |  |  | The C19 outlet low alert of this PDU triggered
|  |  |  | c19OutletLowAlertCleared |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.35 |  | pduIndex, pduName, pduLocation, c19OutletIndex, c19OutletName, c19OutletAlarmState, c19OutletLoadAmp |  |  | The C19 outlet low alert of this PDU cleared
|  |  |  | c19OutletLowAlertThreshChanged |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.36 |  | pduIndex, pduName, pduLocation, c19OutletIndex, c19OutletName, c19OutletLoadAmpLowAlertThresh |  |  | The C19 outlet low alert threshold of this PDU changed
Hide |  |  |  | c19OutletPeakAmpChanged |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.37 |  | pduIndex, pduName, pduLocation, c19OutletIndex, c19OutletName, c19OutletPeakAmp |  |  | The C19 outlet peak Amp of this PDU changed
Hide |  |  |  | c19OutletPeakAmpReseted |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.38 |  | pduIndex, pduName, pduLocation, c19OutletIndex, c19OutletName, c19OutletPeakAmp |  |  | The C19 outlet peak Amp of this PDU reset
|  |  |  | c19OutletCumulativeEnergyReseted |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.39 |  | pduIndex, pduName, pduLocation, c19OutletIndex, c19OutletName, c19OutletCumulativeEnergy |  |  | The C19 outlet cumulative energy of this PDU reset
|  |  |  | tempHumiSenosorConnLost |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.40 |  | pduIndex, pduName, pduLocation, tempHumiSensorIndex, tempHumiSensorType, tempHumiSensorName, tempHumiSensorLocation |  |  | The temperature or temperatue-humidity sensor disconnected
|  |  |  | tempSesnorUpperAlarmTriggered |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.41 |  | pduIndex, pduName, pduLocation, tempHumiSensorIndex, tempHumiSensorType, tempHumiSensorName, tempHumiSensorLocation, tempHumiSensorAlarmState, tempSensorValueStr |  |  | The temperature upper alarm triggered
|  |  |  | tempSesnorUpperAlarmCleared |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.42 |  | pduIndex, pduName, pduLocation, tempHumiSensorIndex, tempHumiSensorType, tempHumiSensorName, tempHumiSensorLocation, tempHumiSensorAlarmState, tempSensorValueStr |  |  | The temperature upper alarm cleared
|  |  |  | tempSensorUpperAlarmThreshChanged |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.43 |  | pduIndex, pduName, pduLocation, tempHumiSensorIndex, tempHumiSensorType, tempHumiSensorName, tempHumiSensorLocation, tempSensorUpperAlarmThresh |  |  | The temperature upper alarm threshold changed
Hide |  |  |  | tempSesnorLowerAlarmTriggered |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.44 |  | pduIndex, pduName, pduLocation, tempHumiSensorIndex, tempHumiSensorType, tempHumiSensorName, tempHumiSensorLocation, tempHumiSensorAlarmState, tempSensorValueStr |  |  | The temperature lower alarm triggered
Hide |  |  |  | tempSensorLowerAlarmCleared |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.45 |  | pduIndex, pduName, pduLocation, tempHumiSensorIndex, tempHumiSensorType, tempHumiSensorName, tempHumiSensorLocation, tempHumiSensorAlarmState, tempSensorValueStr |  |  | The temperature lower alarm cleared
Hide |  |  |  | tempSesnorLowerAlarmThreshChanged |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.46 |  | pduIndex, pduName, pduLocation, tempHumiSensorIndex, tempHumiSensorType, tempHumiSensorName, tempHumiSensorLocation, tempSensorLowerAlarmThresh |  |  | The temperature lower alarm threshold changed
|  |  |  | humiSensorUpperAlarmTriggered |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.47 |  | pduIndex, pduName, pduLocation, tempHumiSensorIndex, tempHumiSensorType, tempHumiSensorName, tempHumiSensorLocation, tempHumiSensorAlarmState, humidSensorValueStr |  |  | The relative humidity upper alarm triggered
|  |  |  | humiSensorUpperAlarmCleared |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.48 |  | pduIndex, pduName, pduLocation, tempHumiSensorIndex, tempHumiSensorType, tempHumiSensorName, tempHumiSensorLocation, tempHumiSensorAlarmState, humidSensorValueStr |  |  | The relative humidity upper alarm cleared
|  |  |  | humiSensorUpperAlarmThreshChanged |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.49 |  | pduIndex, pduName, pduLocation, tempHumiSensorIndex, tempHumiSensorType, tempHumiSensorName, tempHumiSensorLocation, humiSensorUpperAlarmThresh |  |  | The relative humidity upper alarm threshold changed
Hide |  |  |  | humiSensorLowerAlarmTriggered |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.50 |  | pduIndex, pduName, pduLocation, tempHumiSensorIndex, tempHumiSensorType, tempHumiSensorName, tempHumiSensorLocation, tempHumiSensorAlarmState, humidSensorValueStr |  |  | The relative humidity lower alarm triggered
Hide |  |  |  | humiSensorLowerAlarmCleared |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.51 |  | pduIndex, pduName, pduLocation, tempHumiSensorIndex, tempHumiSensorType, tempHumiSensorName, tempHumiSensorLocation, tempHumiSensorAlarmState, humidSensorValueStr |  |  | The relative humidity lower alarm cleared
Hide |  |  |  | humiSensorLowerAlarmThreshChanged |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.52 |  | pduIndex, pduName, pduLocation, tempHumiSensorIndex, tempHumiSensorType, tempHumiSensorName, tempHumiSensorLocation, humiSensorLowerAlarmThresh |  |  | The relative humidity lower alarm threshold changed
NEW |  |  |  | pduDisconnected |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.53 |  | pduIndex, pduName, pduLocation,pduConnState, pduActivation |  |  | The pdu is disconnected
NEW |  |  |  | pduConnectionRestored |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.54 |  | pduIndex, pduName, pduLocation,pduConnState, pduActivation |  |  | The pdu's connection is restored
NEW |  |  |  | pduMainStatusAlarmTriggered |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.55 |  | pduIndex, pduName, pduLocation,pduConnState, pduActivation |  |  | The pduMainStatus alarm triggered
NEW |  |  |  | pduMainStatusAlarmCleared |  |  |  |  | .1.3.6.1.4.1.34550.20.2.2.56 |  | pduIndex, pduName, pduLocation,pduConnState, pduActivation |  |  | The pduMainStatus alarm cleared
Note on E11: Ed: remove, reserve oid
Note on E181: Ed.Chan: rename to prevent duplicate object definition
Note on E182: Ed.Chan: rename to prevent duplicate object definition
Note on E194: Ed.Chan: rename to prevent duplicate object definition
Note on E195: Ed.Chan: rename to prevent duplicate object definition
Note on L94: Ed.Chan: Changed from DisplayString(0..4)